## Instructions
Instructions
Appendix C must be submitted in Excel format on CD.
Two (2) complete hard copy of this Appendix C must accompany your bid.
Write your company name and contract number on the CD.
Do not make any changes to the electronic Excel file formats, including adding rows or colums, changing column headers, inputting text in numeric fields. Comments made on the spreadsheet will be ignored.
Save your changes to this document under the following filename: GSS13235-WATER_TREAT
Enter all information directly into the relevant Excel spreadsheet cells in "number" (two-place decimal), not "currency" or other format unless otherwise stated. That is, omit dollar signs, commas, and any other non-essential symbols.
Enter "N/A" to indicate not available. Enter "0" to indiciate there is no charge. Cells left blank will be interpreted as "NO BID".
Please only fill in areas highlighted in yellow.
See individual tabs for additional instructions.
PROPOSALS MUST BE RECEIVED NO LATER THAN 1:00 P.M. ON Tuesday, January 8, 2013 AT:
State of Delaware, Government Support Services Attn: Contracting, GSS13235-WATER_TREAT 100 Enterprise Place, Suite 4 Dover, DE 19904

## Vendor Information
VENDOR INFORMATION
ADDITIONAL INSTRUCTIONS:
Input Point of Contact Information for this solicitation. Vendor Name will transfer over to each additional tab in this Appendix.
Vendor Name:
Vendor Address:
City, State, Zip Code:
Contact Person:
Phone number:
Email:
SECTIONS BID
Vendors are not required to bid on all sections in order to be considered. Notate for each section whether you are submitting a bid or no bid.
Section | Bid/No Bid
DFM
DOC
SERVICE AREA
Please identify which count(y/ies) you are able to service.
County | Yes or No
New Castle
Kent
Sussex
ACCOUNT MANAGER
Please identify an Account Manager and Secondary Contact to serve as the POCs for regular day-to-day service requests as well as a phone number to call for Emergency Requests.
Account Manager:
Account Manager phone:
Account Manager email:
Secondary Contact:
Secondary Contact phone:
Secondary Contact email:
Emergency Requests phone:
LABOR RATE
Identify the hourly labor rate for service
Labor Rate:

## Chemicals
CHEMICALS
COOLING TOWER
1. Corrosion Inhibitor
Name
Generic Type
Active Compontents
ppm Product in Circulating Water
Dosage, lbs/1000 Gallons of Bleed
Test type and limits
Delivered cost/lb
Package size
2. Biocide
Name
Generic Type
Active Components
ppm Product in Circulating Water
Dosage, lbs/1000 Gallons of Volume
Dosage, lbs/1000 Gallons of Bleed
Test type and limits
Delivered cost/lb
Package size
3. Biocide
Name
Generic Type
Active Components
Dosage, lbs/1000 Gallons of Volume
Dosage, lbs/1000 Gallons of Bleed
Test type and limits
Delivered cost/lb
Package size
CLOSED SYSTEMS - HOT WATER
4. Corrosion Inhibitor
Name
Generic Type
Active Components
ppm Product in Circulating Water
Dosage, lbs/1000 Gallons of Volume
Test type and limits
Delivered cost/lb
Package size
CHILL WATER
5. Corrosion Inhibitor
Name
Generic Type
Active Components
ppm Product in Circulating Water
Dosage, lbs/1000 Gallons of Volume
Test type and limits
Delivered cost/lb
Package size
DUAL TEMPERATURE
6. Corrosion Inhibitor
Name
Generic Type
Active Components
ppm Product in Circulating Water
Dosage, lbs/1000 Gallons of Volume
Test type and limits
Delivered cost/lb
Package size
STEAM SYSTEMS
7. All in one Treatment
Generic Type
Active Components
ppm Product per ppm Hardness
ppm Product per ppm Oxygen
ppm Product in Boiler
Test type and limits
Delivered cost/lb
Package size
8. All in one Treatment (FDA aproved)
Generic Type
Active Components
ppm Product per ppm Hardness
ppm Product per ppm Oxygen
ppm Product in Boiler
Test type and limits
Delivered cost/lb
Package size

## Basis for Calculations
BASIS FOR CALCULATIONS (OPERATING DATA)
OPEN RECIRCULATING COOLING TOWERS
| New Castle |  | Kent |  | Sussex
| Summer | Winter | Summer | Winter | Summer | Winter
Total tons | 2351 | 1600 | 3215 | 2575 | 310 | 75
Bleedoff rate, gpd | 18684 | 9342 | 26220 | 13432 | 1123 | 100
Cycles | 6 | 6 | 3.5 | 3.5 | 6 | 6
Volume, gal | 7150 | 7150 | 17300 | 13500 | 1575 | 225
CLOSED SYSTEMS
Hot makeup, gpy | 300 |  | 300 |  | 100
Chill makeup, gpy | 300 |  | 300 |  | 100
Dual Temp makeup, gpy | 100 |  | 100 |  | 50
STEAM SYSTEMS (Capitol Police)
Steam produced, lbs/yr | 500000
Feedwater flow, lbs/yr | 510000
% Makeup | 5
Makeup Temperature, o F | 200+
Feedwater hardness, ppm | <1
Operating period, days | 180

## Control Limits & Raw Water Anal
CONTROL LIMITS AND RAW WATER ANALYSIS
OPEN COOLING WATER SYSTEMS
| New Castle | Kent | Sussex
Total Hardness, ppm as CaCO3
Calcium Hardness, ppm as CaCO3
Total Alkalinity, ppm as CaCO3
Inhibitor, ppm as Constituent
pH
Total Plate Count, Colonies/ml | <10,000 | <10,000 | <10,000
Corrosion Rate, mpy | <3 MS, <.2 Cu | <3 MS, <.2 Cu | <3 MS, <.2 Cu
Langeliers Index (LSI) | <3 | <3 | <3
Cycles
Other
HOT WATER SYSTEMS
Total Alkalinity, ppm as CaCO3
Conductivity, micromhos
Inhibitor, ppm as Constituent
Corrosion Rate, mpy | <1 MS, <.1 Cu | <1 MS, <.1 Cu | <1 MS, <.1 Cu
CHILL WATER SYSTEMS
Total Alkalinity, ppm as CaCO3
Conductivity, micromhos
Inhibitor, ppm as Constituent
Corrosion Rate, mpy | <1 MS, <.1 Cu | <1 MS, <.1 Cu | <1 MS, <.1 Cu
Total Plate Count, Colonies/ml | <1,000 | <1,000 | <1,000
DUAL TEMP SYSTEMS
Total Alkalinity, ppm as CaCO3
Conductivity, micromhos
Inhibitor, ppm as Constituent
Corrosion Rate, mpy | <1 MS, <.1 Cu | <1 MS, <.1 Cu | <1 MS, <.1 Cu
Total Plate Count, Colonies/ml | <1,000 | <1,000 | <1,000
STEAM GENERATORS
Softener Hardness, ppm as CaCO3
Feedwater Hardness, ppm as CaCO4
Boiler Water
p Alkalinity, ppm as CaCO3
M Alkalinity, ppm as CaCO3
Phosphate, ppm as PO4
Sulfite, ppm as SO3
Conductivity, micromhos (unneutralized)
Cycles on Makeup/Feedwater
Condensate pH
Other, ppm as ?
RAW WATER ANALYSIS
| New Castle | Kent (1) | Kent (2) | Kent (3) | Sussex
Total Hardness as CaCO3
Calcium Hardness, ppm as CaCO3
Total Alkalinity, ppm as CaCO3
Conductivity, micromhos
Silica, as SiO2
Sulfate, as SO4
Chloride, as NaCl
Other

## Site Visit Contacts
DFM SITE VISIT CONTACTS
Location | Contact
| Name | Phone
DFM - New Castle | Michael Jacobs | 739-4611
DFM - Kent | Rob Kapp/Bill Gibbons | 739-4611
DFM -Sussex | Don Gerardi/Tony Fasano | 856-5818
DOC SITE VISIT CONTACTS
Location | Contact
| Name | Phone
DOC - HRYCI | Doug Rodgers | 429-7755
DOC- JTVCC | Mike Lenigan | 739-4379
DOC - MCCC | Mike Lenigan | 739-4379
DOC - SCI & SVOP | Ron Zawora | 856-5265
DHSS SITE VISIT CONTACTS
Location | Contact
| Name | Phone
DHSS - Herman Holloway | Tim Read | 255-4488
DHSS - Hudson SSC
DHSS - Porter SSC
DHSS - Bissell Hospital | Michael Topolski | 528-4983
DOS SITE VISIT CONTACTS
Location | Contact
| Name | Phone
DOS - Veterans Home | Charles Spray | 424-6000
DSCYF SITE VISIT CONTACTS
Location | Contact
| Name | Phone
NCCDC 963 Centre Rd. Wilmington, DE 19805 | Chuck Boring Robert Harrity | 633-3108 993-4880
Ferris School 959 Centre Rd. Wilmington, DE 19805 | Zack Hasty Robert Harrity | 993-3828 993-4880
Main Admin Bldg. 1825 Faulkland Rd. Wilmington, DE 19805 | Merle Wanamaker Robert Harrity | 633-2515 993-4880
Snowdon Cottage 1825 Faulkland Rd. Wilmington, DE 19805 | Bill Hedrick Robert Harrity | 995-8292 993-4880
Grace Cottage 1825 Faulkland Rd. Wilmington, DE 19805 | Bill Hedrick Robert Harrity | 995-8292 993-4880
Mowlds Cottage 1825 Faulkland Rd. Wilmington, DE 19805 | Bill Hedrick Robert Harrity | 995-8292 993-4880
Stevenson House 750 N. Dupont Hwy. Milford, DE 19963 | William Wilson Jeremiah Hasting | 424-8131 424-8132
Terry Children's Center 10 Central Ave. New Castle, DE 19720 | Doug Lyons Kenneth Vanderslice | 256-5637 256-5637

## Pricing - DFM
PRICING - DFM
LUMP SUM BID | NEW CASTLE | KENT | SUSSEX
Tower Inhibitor
Biocide
Biocide
Hot Inhibitor
Chill Inhibitor
Dual Temp Inhibitor
Boiler Treatment
Boiler Treatment (FDA)
Other
Labor
Total
Total all 3 Counties | 0
Other: Please provide details below regarding "Other".
Labor: Identify estimated hours per county per month.
ESTIMATED HOURS PER MONTH
| NEW CASTLE | KENT | SUSSEX

## Pricing - DOC
PRICING - DOC
Howard R. Young Correctional Institution
EQUIPMENT | FACILITY MONTHLY COST
West Side
(2) 200 ton closed loop chiller w/common sump
(1) 400 ton cooling tower
East Side
(2) 250 ton closed loop chiller
(2) 250 ton cooling tower
(4) hot water boiler system
Total:
James T. Vaughn Correctional Center
EQUIPMENT | FACILITY MONTHLY COST
CVOP
(5) 70 ton closed loop chiller
(2) 70 ton cooling tower
(1) hot water boiler system
S-1 Building
(1) 80 ton closed loop chiller
(1) 80 ton cooling tower
(1) hot water boiler system
Total:
Sussex Correctional Institution
EQUIPMENT | FACILITY MONTHLY COST
SVOP
(2) 78 ton closed loop chillers
(2) 78 ton cooling towers
(1) hot water boiler system
Pre-Trial
(2) 345 ton closed loop chillers
(2) 345 ton cooling towers
(1) hot water boiler system
Old Max Building
(1) water softener
(2) steam boilers w/condensate
(3) hot water loop
Total:
Morris Correctional Institution
EQUIPMENT | FACILITY MONTHLY COST
(4) 90 ton closed loop air cooled chillers
(1) hot water boiler system
Total:
Monthly Total - All Facilities: | 0

## Pricing - DHSS
PRICING - DHSS
Herman Holloway Campus
EQUIPMENT | FACILITY MONTHLY COST
Main Admin Bldg - Steam boiler (Bryan) 5200 PPH
T-Building - Hot water boiler (Weil McLain) 490 PPH
Warehouse - Steam boiler (Weil McLain) 1084 PPH
Power Plant - Steam boiler (Bryano) 17662 PPH
Chapel - Hot water boiler (weil McLain) 360 PPH
Maintenance Shop - Steam boiler (Burnham) 3529 PPH
Garden Café - Steam boiler (weil McLain) 1632 PPH
Charles Debnam Bldg. - Steam boiler (Weil McLain) 1632 PPH
Lewis - Hot water boiler (Burnham) 1314 PPH Cooling tower (Recold SPX)
Whitehouse - Hot water boiler (Crown) 152 PPH
Kent & Sussex - Hot water boiler (HB Smith) 5793 PPH Cooling Towers (BAC) (EVAPCO) 250 Tons York Chillers
Mitchell - Hot water boiler (Smith) 652 PPH
Carvel - Hot water boiler (Weil McLain) 2612 PPH Cooling Tower (BAC) 75 Tons York Chiller
Spring - Hot water boiler (HB Smith) 2067 PPH
Biggs - Hot Water (HB Smith) 2840 PPH
Total:
State Service Centers - New Castle
EQUIPMENT | FACILITY MONTHLY COST
Hudson - Hot water boiler (Hydro Therm) 1168 PPH Cooling Tower (EVAPCO)
Porter (Lochnivar Knight) 500 PPH Airstack Chiller 53 tons
Total:
Emily P. Bissell Hospital - New Castle
EQUIPMENT | FACILITY MONTHLY COST
Kewanee Boiler #1 3348 MBh
Kewanee Boiler #2 3348MBh
Total:
Stockley Campus - Sussex
EQUIPMENT | FACILITY MONTHLY COST
(3) Cleaver Brooks Boiler (FLX200-600) 6,000,000 BTU/HR
(2) Cleaver Brooks Boiler (CB100-150) 6,277,000 BTU/HR
(3) 250 Ton Chill Water Closed Loop Systems
Total:
Thurman Adams Service Center - Sussex
EQUIPMENT | FACILITY MONTHLY COST
(3) HB Smith Boiler (18 Series 7) 480,000 BTU/HR
(2) Weil-McLain Boiler (P778-W) 764,000 BTU/HR
100 Ton Chill Water Closed Loop System
(2) 200 Ton Chill Water Closed Loop System
Total:
Ellendale Support Services - Sussex
EQUIPMENT | FACILITY MONTHLY COST
(2) Peerless (EC/ECT-05-175-W/5) 186,000 BTU/HR
Weil-McLain (A/B868) 234,000 BTU/HR
Total:

## Pricing - DHSS (WELL)
PRICING - DHSS
Stockley Campus - Sussex
EQUIPMENT | FACILITY MONTHLY COST
WELL (MAC Center): Water Boy filter system, iron removal, ph, Chlorine
WELL (Main): ph, Chlorine
Total:
Thurman Adams Service Center - Sussex
EQUIPMENT | FACILITY MONTHLY COST
WELL: Water Softener
Total:
Ellendale Support Services - Sussex
EQUIPMENT | FACILITY MONTHLY COST
WELL: No treatment, high iron
Total:

## Pricing - DSCYF
PRICING - DSCYF
Terry Center
EQUIPMENT | FACILITY MONTHLY COST
Cooling tower loop (chiller)
Total:
Stevenson House
EQUIPMENT | FACILITY MONTHLY COST
Closed Loop Heating System
Cooling tower loop (chiller)
Total:
Ferris School
EQUIPMENT | FACILITY MONTHLY COST
Closed Loop Heating System
Cooling tower loop (chiller)
Total:
New Castle County Detention Center
EQUIPMENT | FACILITY MONTHLY COST
(1) Heat Pump Loop
Total:
Administration Building
EQUIPMENT | FACILITY MONTHLY COST
(1) Heat Pump Loop
Total:
Snowden Cottage
EQUIPMENT | FACILITY MONTHLY COST
(1) closed loop heating system
Total:
Mowlds Cottage
EQUIPMENT | FACILITY MONTHLY COST
(1) closed loop heating system
Total:
Grace Cottage
EQUIPMENT | FACILITY MONTHLY COST
(1) closed loop heating sytem
Total:

## Pricing - DOS
PRICING - DOS
Veterans Home
EQUIPMENT | FACILITY MONTHLY COST
Heating Hot Water
Chilled Water
Total:
EQUIPMENT | FACILITY MONTHLY COST
Total:
EQUIPMENT | FACILITY MONTHLY COST
Total: